## Cover
PROPOSED RENOVATION AT HEAD OFFICE OF AB RWANDA PLC
TENDER BILLS OF QUANTITIES
CONSULTANTS.
ALENSO LTD
All engineering solution
Execution of the projects and other related engineering services
alensoltd@outlook.com / butumwaa@gmail.com
August 2026

## Summary
Project: PROPORSED RENOVATION FOR AB RWANDA - HEAD OFFICE
CLIENT: AB RWANDA
LOCATION: NYARUGENGE
MAIN SUMMARY
Brief Description | Units | Qty | Rate | Amount
PRELIMINARIES |  |  |  | 0
FIT OUT WORKS |  |  |  | 0
ELECTRICAL |  |  |  | 0
ICT |  |  |  | 0
HVAC |  |  |  | 0
SECURITY |  |  |  | 0
PLUMBING |  |  |  | 0
TOTAL |  |  |  | 0
Unconditional 2% Discount |  |  |  | 0
DISCOUNTED TOTAL |  |  |  | 0
contingencies @ 3% |  |  |  | 0
TOTAL VAT EXCLUSIVE |  |  |  | 0
VAT @ 18% |  |  |  | 0
GRAND TOTAL TO TENDER FORM |  |  |  | 0

## Preliminaries
Project: PROPORSED RENOVATION FOR AB RWANDA - HEAD OFFICE
CLIENT: AB RWANDA
LOCATION: NYARUGENGE
BILL No.01 - PRELIMINARIES
Item No | Description | Units | Qty | Rate | Amount-Rwf.
PRELIMINARIES
Site Establishment (Fixed Costs)
| Signs / Notice Boards / Traffic- | Item | 1 |  | 0
| Temprary hoarding- | Item | 1 |  | 0
Insurance
| Contractors All Risk - | Item | 1 |  | 0
Site Security (Time Based)
| Security staff (external company) | Months | 1 |  | 0
| Lighting & Watching | Months | 1 |  | 0
Tools, Equipment & Plants ( Time based)
| Scaffolds | Months | 1 |  | 0
Completion and post-completion requirements -
| As built drawings - MANDATORY | Item | 1 |  | 0
| Building/ deep cleaning | Months | 1 |  | 0
PPE
| Being Ppe for employees with overall | Item | 1 |  | 0
| TOTAL TO MAIN SUMMARY |  |  |  | 0

## Fit outs
Project: PROPORSED RENOVATION FOR AB RWANDA - HEAD OFFICE
CLIENT: AB RWANDA
LOCATION: NYARUGENGE
BILL No.02 - FITOUTS
Item No. | Brief Description | Units | Qty | Rate-Rwf | Amount - Rwf
DEMOLITIONS AND ALTERATIONS
Preambles
The contractor shall make sure while demolishing that any part of the buiding structural fabric is not damaged
All exisitng services shall be carefully terminated and reconnected after demolition works
The rates of demolition works shall include for making good disturbed parts and carting away arising debris.
The contractor shall ensure that his workforce uses tools for demolitions and will not cause any disturbamce and /or nuisance to other building users
The contractor shall submit proposed methodology for demolition works for project managers review and approval prior to commencement of demolition works.
The contractor shall prepare demolitions schedule for all demolished items and the same shall be signed for confirmation by the project manager before any materials is handed over to the client / property managers
Installation Labour charge applied for the Re-used material
Walls
Carefully demolish existing masonry walls - Hollow concrete blocks. Cart away debris. Make good disturbed parts
Generally
| 200 mm thick | M2 | 4.32 |  | 0
| Carefully demolish existing aluminium partition walls - to be reused. | M2 | 64.8 |  | 0
Floor and wall Tile
| Carefully remove existing tiles and hack screed backing; remove debris from site. To handover salvaged material to client | M2 | 60.56 |  | 0
Floor finish
| Carefully remove added floor finish without damaging main floor finish of terrazo ; remove debris from site. To handover salvaged material to client | M2 | 138.7 |  | 0
Wall cladding
| Carefully remove existing timber/wood pannel cladded on wall and column ; remove debris from site. To handover salvaged material to client | Item | 1 |  | 0
| Carried forward to next page |  |  |  | 0
| Brought forward from previous page |  |  |  | 0
Broken glass
| Carefully remove broken glasses to be replaced ; remove debris from site | Item | 1 |  | 0
Ply wood ceiling
| Carefully remove existing plywood ceiling to create holes for reaching out the slab soffit only for new gypsum ceiling (N.B. existing ceiling frame will remain between slab soffit and new ceiling means it will not be demolished) ; remove debris from site. To handover salvaged material to client | Item | 1 |  | 0
Building Services
| Terminate / Disconnect, take down existing Mechanical and Electrical installations which is not necessary in both new area and existing offices and branch. | item | 1 |  | 0
| ELEMENT TOTAL TO FITOUTS SUMMARY |  |  |  | 0
WALLING AND PARTITIONING
DRY WALLS
Gypsum board Partitions
Gypsum board drywall system as Knauf or Approved equal of 12.5mm both side of 75 X 50 x 2mm thick galvanized U shaped Studs, in box grid not exceeding 600mm C/C. Board joints taped and filled and skimcoat on all sides. Corners to be treated with L shaped 20 x 20 x 1.2mm thick Galvanised corners piece.
| 100mm thick | M2 | 53.76 |  | 0
Internal- Partitions
Natural anodized aluminium sections :box profile or angle sections plugged to walls / floor: Hydro Aluminium extrusion or equal and approved: metred joints: complete with 6.38mm thick clear laminated safety glass with sandblast film beadings and butterfly to match, and glazing rubber. Aluminium sections 2mm thick minimum. RAL No 9005 (jet black) to architects specification and approval.
| 100mm thick | M2 | 97.2 |  | 0
| relocation of existing demolished partitions to new place and fix with all accessories | M2 | 79.5 |  | 0
Masonry work
Hollow Cement blocks in cement and sand (1:3) mortar reinforced with Gauge 16 hoop iron in every alternate course
| 200mm thick | M2 | 42.7 |  | 0
| ELEMENT TOTAL TO FITOUTS SUMMARY |  |  |  | 0
DOORS, WINDOWS HAND RAIL
Reinstallation
| labour to install doors . Provide for new locks, hinges and door closers | No | 8 |  | 0
NEW DOORS
Aluminium Framed
Supply and fix grey powder coated aluminium glazed doors complete with 8,38mm thick clear laminated glass, handle and accessories: all to architects detailed drawing
| Overal size 900x2400 | No | 5 |  | 0
Timber Doors
Internal: Flash doors
Renovation of existing toilet door include painting and vernishing and complete door finish
| 900 x 2400mm high | No | 2 |  | 0
Steel Door
| Consider reusing steel door + renovation and fix one side where necessary | No | 3 |  | 0
| Carried forward to next page |  |  |  | 0
| Brought forward from previous page |  |  |  | 0
IRON MONGERY
Supply and fix the following ironmongery with matching screws to as suplied by ASA ABLOY or other wqual and approved:
| Aluminium satin anodised kick plate ( Ref: Union KP- 800 - 200 AS ) | No | 2 |  | 0
Signage
| Stainless steel printed door signs ( Ladies, gents, Kitchenette) size 100 x 100mm | No | 2 |  | 0
Hinges
| Ball bearing butt hinges: stainless steel- 100mm | Pairs | 21 |  | 0
| Door closer- as Yale: 2000 series: concealed | No | 10 |  | 0
| Black matt cylinder locks complete with matching handles to architects approval- Ref to Assa Abloy catalogue | No | 10 |  | 0
| Carried forward to next page |  |  |  | 0
| Brought forward from previous page |  |  |  | 0
WINDOWS
METAL WINDOW
| Repair of existing windows for better ventilation,openings, brush rust, repair and replace of broken glasses | Item | 1 |  | 0
| Renovation of existing windows for better ventilation and mae it sliding window | Item | 1 |  | 0
Painting Existing frames of window, door, handrail on balcony and handrail stair
| Provide for spray grey paint to match powder coated aluminium | Item | 1 |  | 0
| ELEMENT TOTAL TO FITOUTS SUMMARY |  |  |  | 0
FLOOR FINISHES
Beds
Screed: 1:3- Cement and sand to receive floor tiles
| Trowel finished | SM | 5.5 |  | 0
Tile work
Porcelain floor tiles: None slip: full body: laid in regular patterns
| 400 x 400 x 10mm thick in toilet | SM | 5.5 |  | 0
Supply and fix SPVC Floor tile bedded and jointed in approved adhesive and color should be approved by the client
| 1200 x 200 x 4mm thick | SM | 153.5205 |  | 0
| Repair, and replace damaged floor tile in corridor, the same color as existing | SM | 8.5 |  | 0
| ELEMENT TOTAL TO FITOUTS SUMMARY |  |  |  | 0
WALL FINISHES
Plaster
Cement, lime sand : 1:2: 6, applied in 2 coats to masonry surfaces to receive paint: Steel trowelled
| Generally: 15mm thick | SM | 98 |  | 0
Cement and Sand ( 1: 4) to masonry surfaces : to receive wall tiles:
| Generally 15mm thick | SM | 44.8 |  | 0
| Repair existing wall and column plaster finish to make the wall texture finish and smoth before painting | Item | 1 |  | 0
Painting & Decoration
Internally
Prepare , skim and appply three coats of first quality paint: Silk vinyl to :
| Masonry walls, Gypsum board Surfaces,Previously painted Surfaces in all offices and balcony per arch details and approval | SM | 2883.9 |  | 0
Tiling
Imported Ceramic tiles : Wall tiles: Glazed Surface: In regular patters / Dado: Measured to include stainless corner strip
To wall with approved adhesive: pointed with approved grout to match
| 800 x 400 x 10mm thick | M2 | 44.8 |  | 0
| ELEMENT TOTAL TO FITOUTS SUMMARY |  |  |  | 0
CEILING FINISHES
Gypsum
75x35x1.5mm thick galvanised steel u shaped ceiling studs bolted onto slab soffit. Gypsum plasterboard screwed onto studs using gypsum screws
| 9mm thick gypsum ceiling plasterboard at new extended area, CEO Office and reception area. | SM | 198.5 |  | 0
| Ceiling plasterboard repair that could be damaged while changing the electrical installation | Item | 1 |  | 0
Painting
Prepare and apply three coats of silk matt paint to gypsum surfaces:
| Generally | SM | 198.5 |  | 0
| Prepare and apply two coats of silk matt paint to of existing ceiling | SM | 980 |  | 0
| ELEMENT TOTAL TO FITOUTS SUMMARY |  |  |  | 0
JOINERY FITTINGS
Kitchen cabinets
Low level kitchen cabinets comprising 20mm thick veneered water proof M.D.F board on sides; dividers; shelves and doors: 20mm thick granite top;mapla hinges, door contact All to architects detailed design
| 600 x 900mm high | LM | 2.5 |  | 0
High level kitchen cabinets plugged to wall comprising 20mm thick veneered MDF board in shelves, sides and divisions. 8mm thick clear toughened glass in doors. Iron mongery deemed to be included. All to architects detailed designs and specification.
| Size 450 x 1200mm high | LM | 2.5 |  | 0
| Repair of existing Low level kitchen cabinets omprising 20mm thick veneered water proof M.D.F board; dividers; shelves and doors: mapla hinges, door contact | Item | 1 |  | 0
Coffee and tea making table
Low level kitchen cabinets comprising 20mm thick veneered water proof M.D.F board on sides; dividers; shelves and doors: 20mm thick granite top;mapla hinges, door contact All to architects detailed design
| 600 x 900mm high | LM | 2.5 |  | 0
Water bottles shelves
| 600*2400 high finished marine boards as fixed on 40*40*1.5 SHS frames | LM | 3.5 |  | 0
| ELEMENT TOTAL TO FITOUTS SUMMARY |  |  |  | 0
FITOUTS SUMMARY
| DEMOLITIONS |  |  |  | 0
| PARTITIONS |  |  |  | 0
| DOORS & WINDOWS |  |  |  | 0
| FLOOR FINISHES |  |  |  | 0
| WALL FINISHES |  |  |  | 0
| CEILING FINISHES |  |  |  | 0
| JOINERY FITTINGS |  |  |  | 0
| TOTAL FOR BILL CARRIED TO GRAND SUMMARY |  |  |  | 0

## ELECTRICAL
Project: PROPORSED RENOVATION FOR AB RWANDA - HEAD OFFICE
CLIENT: AB RWANDA
LOCATION: NYARUGENGE
BILL No.03 - ELECTRICAL
Item No | Description | Units | Qty | Rate | Amount-Rwf.
POWER RETICULATION
For all items under this element:Supply, fix ,test and commission all equipments and fixtures. Installation to be complete with all necessary accessories to proper working to engineers approval and satisfaction
Distribution Board
Distribution board complete with all Weather proof,Purpose made, lockable; wiring fixing and earthing with 4mm diameter pure electrolytic copper earth rod deep driven to permanent moisture level, copper lamp. 10mm sq green earth lead complete with all accessories.,complete with as per drawing as HARVEN / TRONICS or equivalent and approved
| 8 ways TPN Main board | No | 1 |  | 0
| 1 way TPN 12 ways SPN for ground floor, first floor and second floor | No | 3 |  | 0
| 3 way TPN 8 ways SPN for UPS | No | 1 |  | 0
| 1 way TPN 8 ways SPN for UPS | No | 3 |  | 0
| 1 way TPN 8 ways SPN for Shared service | No | 1 |  | 0
Cables
Supply and lay the following cables as Alfa cables to approval & satisfaction of the engineer
Note: All complete with cable lugs
| 5core x 35mm square PVC Copper, 0.6/1kv; class2 cable | LM | 30 |  | 0
| 4core x 16mm square PVC Copper, 0.6/1kv; class2 cable | LM | 150 |  | 0
| 4core x 6mm square PVC Copper, 0.6/1kv; class2 cable | LM | 15 |  | 0
| Carried forward to next page |  |  |  | 0
| Brought forward from previous page |  |  |  | 0
UPS - REUSE
| Allow for disconnecting existing UPS and reinstall in the new location: 15 KVA | No | 3 |  | 0
MCCBs
Supply and install as Harven or approved equal
| 125 A TPN | No | 1 |  | 0
MCBs
Allow supply,installation of new and testing, re-installation existing MCBs
| 80 A TPN | No | 10 |  | 0
| 32A TPN | No | 3 |  | 0
| 32- Single phase | No | 3 |  | 0
| 16 Single phase | No | 24 |  | 0
| 10 Single phase | No | 10 |  | 0
| DP Switch |  | 10 |  | 0
SPDs
| SPD Class II | No | 3 |  | 0
RCD
| 80 A TPN | No | 3 |  | 0
| ELEMENT TOTAL TO ELECTRICALS SUMMARY |  |  |  | 0
LIGHTING SYSTEMS
Light fittitngs
Supply fix test and commission all light fittings as Tronic Catalogues or approved equal. Installation to be complete with all necessary accessories to proper working to engineers approval and satisfaction
| Recessed type Panel light 600x600mm, Type of Protection: IP 20, Protection Class: II, 34W LED 90lm/w | No | 6 |  | 0
| 12 W LED circular recessed ceiling lights | No | 10 |  | 0
| 5W LED circular recessed ceiling lights double set | No | 20 |  | 0
| 18 Watt drive ceiling recessed profile light | lm | 8 |  | 0
Switching Points
| 1 gang 1 way: 10A SP 250 V switch as legrand or equivalent and approved | No | 6 |  | 0
| 1 gang 2 way: 10A SP 250 V switch as legrand or equivalent and approved | No | 2 |  | 0
| 2 gang 2 way: 10A SP 250 V switch as legrand or equivalent and approved | No | 2 |  | 0
| 2 gang 1 way: 10A SP 250 V switch as legrand cariva or equivalent and approved | No | 1 |  | 0
| Carried forward to next page |  |  |  | 0
| Brought forward from previous page |  |  |  | 0
Lighting Points /Wiring
The cable should have PVC/XPLE insulation and shield, with copper conductors, tested and approved: supply and fix:
| Lighting Wiring from miniature circuit breakers, using 3x1.5 mm sq Flexible Cables drawn in 20mm upvc conduits. complete with switch boxes, junction boxes, couplers, bends and any other necessary conduiting accessories | Roll | 3.5 |  | 0
| Replace existing Lighting Wiring from miniature circuit breakers, using 3x1.5 mm sq Flexible Cables drawn in 20mm upvc conduits. complete with switch boxes, junction boxes, couplers, bends and any other necessary conduiting accessories | Roll | 30 |  | 0
| ELEMENT TOTAL TO ELECTRICALS SUMMARY |  |  |  | 0
POWER POINT
Supply fix test and commission all equipments and fixtures. Installation to be complete with all necessary accessories to proper working to engineers approval and satisfaction. All existing socket should be reconnected
WIRING
The cable should have PVC/XPLE insulation and shield, with copper conductors, tested and approved, supply and fix:
Socket outlet Points
| Socket Wiring from 16A miniature circuit breakers, using 3x2.5 mm sq drawn in 25mm upvc conduits. complete with switch boxes, junction boxes, couplers, bends and any other necessary conduiting accessories (This is for all new additional socket and change the supplier pass through aluminium profile) | Roll | 30 |  | 0
Sockets outlets / fittings
Note: All sockets must be universal & switched
| Twin Power socket outlet, 16A, 250V 2P+E, Legrand Sockets for Standard Raw power socket | No | 56 |  | 0
| Twin Power socket outlet, 16A, 250V 2P+E, Legrand Sockets for None Standard Clean power socket | No | 56 |  | 0
| Allow labor cost for labeling existing power socket after testing and comfirm wether the supply is from Normal current or UPS | FF | 1 |  | 0
| ELEMENT TOTAL TO ELECTRICALS SUMMARY |  |  |  | 0
CABLE MANAGEMENT
Trunking-
PVC trunking: TWO compartments:complete with cover , sockets faceplates,end caps, bends and any other accessories as Legrand or approved equal
| 150 x 50mm deep varies as per circuit line considerations | LM | 420 |  | 0
| 20 x 20mm deep varies as per circuit line considerations | LM | 95 |  | 0
Cable Tray
Purpose made perfornated stainless steel cable tray fixed to slab soffit with M10 rods
| 150 x 50mm | LM | 120 |  | 0
| ELEMENT TOTAL TO ELECTRICALS SUMMARY |  |  |  | 0
SUMMARY
| POWER RETICULATION |  |  |  | 0
| LIGHTING SYSTEM |  |  |  | 0
| POWER POINTS |  |  |  | 0
| CABLE MANAGEMENT |  |  |  | 0
| TOTAL ELECTRICALS TO MAIN SUMMARY |  |  |  | 0

## ICT
Project: PROPORSED RENOVATION FOR AB RWANDA - HEAD OFFICE
CLIENT: AB RWANDA
LOCATION: NYARUGENGE
BILL No.04 - ICT
Item No. | Brief Description | Units | Qty | Rate-Rwf | Amount - Rwf
STRUCTURED CABLING
Supply , install, test and commission the entire structured cabling system to engineers approval and satisfaction.
Patch Panels
| Giganet Category 6 UTP 23″ 48Port Patch panel high-speed data transmission | No | 2 |  | 0
IT Switch
| 48 Port 10/100/1000mbps CISCO 2960 /24PC/L/ manageable switch: 10/100/POE+2T/SFP/LAN baseimage | No | 2 |  | 0
Data Sockets
| Dual Data Socket type RJ45 with 2Max Modules complete with face plates | No | 56 |  | 0
Data Cables
| CAT6 SFTP copper cable for structured cabling as Siemon with 16 yrs waranty | LM | 915 |  | 0
Patch Codes
Extra over data cables in patch codes complete with termination heads
| 3M long | No | 28 |  | 0
| 1M long | No | 28 |  | 0
| Lumpsum for rearranging and re connecting existing IT in workstation | ff | 1 |  | 0
| TOTAL ICT TO BILL SUMMARY |  |  |  | 0

## HVAC
Project: PROPORSED RENOVATION FOR AB RWANDA - HEAD OFFICE
CLIENT: AB RWANDA
LOCATION: NYARUGENGE
BILL No.05 -HVAC
Item | Description/Specification | Unit | Qty | Unit Price (RWF) | Amount (RWF)
The contractor shall supply, install, test and commission to the satisfaction of the engineer the following
OUTDOOR UNIT
| High efficiency heat pump system VRV outdoor unit, dimensions (1240*1690*760)mm*1,net weight(237*1)kg. Mode; independent unit , cooling capacity (61.6KW),220,000BTU/h, heat capacity (61.6KW) rated power max.(16.76KW), fan type : propeller fan, air flow rate(hight) 320*1 m3/min, drive; DC INVERTER. Pipe connection ; Liquid pipe 16 mm and gas pipe 28.58 mm. Sound pressure level ;(cooling 64.5dBA)(heating 65.5dBA), sound power level (cooling 86dBA) (heating 88dBA). comminucation cables (2c*1.0-1.5)No.mm2 (VCTF-SB) ,Refrigirant name R410A, Precharged amount (13,5)kg, (29,8) lbs, GWP 2087.5 , t-CO2eq 28,2 , Control Electronic expantion valve. Refrigerant oil typeFVC68D(PVE), charge 3900 cc, power supply ø,V,Hz (380-415,3,50), number of maximum connect table indoor units 10. Daikin or equivalent | No | 1 |  | 0
| Isolator switch |  | 4 |  | 0
Electrical Works
| Allow for associated electrical works including but not limited to wiring from local isolators provided by others within one meter to all indoor units, outdoor units and control system. Allow for labelling all the circuits and equipment. | No's | 1 |  | 0
| Controller/Thermostat: Capable of concurrent control of temperature and humidity to ensure both specified requirements are continually met | No's | 7 |  | 0
| Return air Grille : Air extraction grille 600x600mm, 130 LPS at Noise Criteria less than or equal to 15 | No's | 7 |  | 0
| Carried forward to next page |  |  |  | 0
| Brought forward from previous page |  |  |  | 0
Supplying, installing, test and commissioning VRF Indoor Casette Unit
| Complete set VRF Indoor 4 way Ceiling Casette AC unit with cooling capacity: 9,000,000BTU/HR dim;600x600mm. Daikin or equivalent | No | 2 |  | 0
| Complete set VRF Indoor 4 way Ceiling Casette AC unit with cooling capacity: 18,000,000BTU/HR dim;600x600mm. Daikin or equivalent | No | 2 |  | 0
| Complete set VRF Indoor 4 way Ceiling Casette AC unit with cooling capacity: 24,000,000BTU/HR dim;600x600mm. Daikin or equivalent | No | 1 |  | 0
| Complete set VRF Indoor 4 way Ceiling Casette AC unit with cooling capacity: 36,000,000BTU/HR dim;600x600mm. Daikin or equivalent | No | 2 |  | 0
| Insulated Duct work: Rectangular ducts of Galvanized steel of 22 SWG/ 0.8mm thickness, with 25mm thick thermal insulation protected by Aluminum sheet covering (Size varies as per the design) | No | 20 |  | 0
| Cost for relocating the existing indoor unit and fix it in appropriate area in the room for proper service | FF | 2 |  | 0
| AIR COLLER : Symphony Diet 22i Personal Air Cooler Tower air cooler for rooms up to 14 sqm Full function remote with 7-hour timer,empty water-tank alarm, High efficiency honeycomb pad, Personal Cooler with powerful blower, Large 22L water-tank capacity, Remote control for convenience | No's | 2 |  | 0
TOTAL HVAC TO BILL SUMMARY |  |  |  |  | 0

## Security
Project: PROPORSED RENOVATION FOR AB RWANDA - HEAD OFFICE
CLIENT: AB RWANDA
LOCATION: NYARUGENGE
BILL No.06 -SECURITY
Item No | Brief Description | Units | Qty | Rate- Rwf | Amount-Rwf
Pricing Notes
Supply,Install test and commitioning security system, including CCTV cameras, motion detectors, access control systems, and a central monitoring unit. The system shall feature high-resolution cameras with night vision, tamper-proof housings, and remote access capabilities via mobile or web platforms, and full configuration for integration with the security system, ensuring compliance with manufacturer standards.
1 | All hard drives to be supplied to be checked for warranty validation.
2 | All cables to be used in this project shall be tested by RBS.
CCTV SURVELLANCE
Cameras : HIK Vision
| 8 Mega pixels: IP Dome Camera colovue | No | 1 |  | 0
| 8 Mega pixels: IP Bullet Camera colovue | No | 4 |  | 0
Cabling
| High-quality Outdoor CAT 6e FTP Cabling to all camera points, complete with required accessories. The cables shall be halogen-free, with a durable PVC sheath, meeting fire safety and environmental standards. The specified brand, such as Nexans, Belden, or equivalent, must ensure compliance with project specifications and quality standards. | LM | 305 |  | 0
| 1 Meter CAT6e SFTP patch cords c/w RJ 45 connectors, cable jacks, male/female sockets etc. | No | 7 |  | 0
Configuration
| Equipment Cabling and Software configuration and any other necessary item. | Item | 1 |  | 0
| switch 16 ports | item | 1 |  | 0
| ELEMENT TOTAL TO SECURITY SUMMARY |  |  |  | 0
AUTO FIRE DETECTION cp plus
DETECTORS
| Smoke detector AW-CSD381, Operating Voltage Range: 9 to 28 VDC Non-polarized, Standby Current ≤120uA@24VDC, Smoke Alarm Sensitivity: 0.1-0.15dB/m. | No | 10 |  | 0
ALERT POINTS
| Manual Call Point AW-D135C, Operating Voltage Range: 18 to 28 VDC, IP Rating IP 30, working current < 4mA | No | 1 |  | 0
| Sounder Beacon AW-D316, Operating Voltage 24VC (20V-28V) operating current <100mA flashing color and frequency: white, 0.5, light output synchronization: meets EN54-23. | No | 1 |  | 0
CABLING
| Fire-Resistant Cable specifically designed to maintain circuit integrity during a fire, ensuring the continuous operation of critical systems such as fire alarms, emergency lighting, and evacuation systems. These cables are constructed with high-temperature insulation and low-smoke, halogen-free sheathing to minimize toxic emissions and ensure safety during a fire. cable 2x1.5 sqmm (100m). | Rlx | 2.5 |  | 0
FIRE FIGHTING
Supply and Install
| 9Kg dry chemical powder fire extinguishers. | No | 1 |  | 0
| 6Kg carbon dioxide powder fire extinguishers. | No | 1 |  | 0
| ELEMENT TOTAL TO SECURITY SUMMARY |  |  |  | 0
ACCESS CONTROL SYSTEMS
Supply and installation
| 183 x 80 x 42mm stand alone ZKTECO F18 as MASTER for Biometric Man trap System with the following specifications: 5000 cards capacity, 3000 finger prints templates, 30,000 transactions, RS 232/485 interface and TFT LCD colour screen. | No | 3 |  | 0
| ZKTECO FR1200 ; RS 485 comm, 324mhz CPU as SLAVE for Biometric Door size 102 x 50 x 37mm | No | 3 |  | 0
| Electromagnetic door contacts | No | 3 |  | 0
| Emergency Break Glass Unit | No | 3 |  | 0
| 3 Amp power supply unit with Back-up | No | 3 |  | 0
| System configuration software, cabling | Item | 1 |  | 0
| ELEMENT TOTAL TO SECURITY SUMMARY |  |  |  | 0
INTRUDER ALARM SYSTEMS
Supply and installation
| Pir Comet Motion Sensor, Coverage at 2.4 m (7’10”) mounting height: 12m x 12m (40’ x 40’) Operating voltage: 9 to 16V Current consumption: 12mA at 12V Alarm contact: 50mA, 24C, N.C Tamper contact: 100mA, 24V, N.C Alarm time: 2.2 seconds minimum Pulse count selection: 1,2 or 3 pulse count Temperature compensation: Automatic, thermistor controlled Optical filtering: White light protection, pigmented lens RF immunity: 20V/m from 10 MHz to 1GHz Operating temperature: -5° to 50°C (23° to 122°F) comatible to be connected on existing | No | 6 |  | 0
| Cost of cabling | Item | 1 |  | 0
| ELEMENT TOTAL TO SECURITY SUMMARY |  |  |  | 0
SECURITY INSTALLATIONS SUMMARY
1 | CCVT |  |  |  | 0
2 | FIRE DETECTION |  |  |  | 0
3 | ACCESS CONTROL |  |  |  | 0
4 | INTRUDER ALARM SYSTEMS |  |  |  | 0
| TOTAL FOR SECURITY INSTALLATIONS TO BILL SUMMARY |  |  |  | 0

## Plumbing
Project: PROPORSED RENOVATION FOR AB RWANDA - HEAD OFFICE
CLIENT: AB RWANDA
LOCATION: NYARUGENGE
BILL No.07 -PLUMBING
Item No. | Brief Description | Units | Qty | Rate-Rwf | Amount - Rwf
PLUMBING AND SANITARY FITTINGS
SANITARY WARE
Supply, Install, test and commission of the following sanitary appliance BS3402 (From approved manufacturer) including all supports, screwing or bolting and connection to floor or walls where necessary complete with all accessories and including angle valves, mixer etc
Water closet
Vitrous White colour: Single piece clouse couple WC with UF Soft close seat cover, Hinges, Dual flush cistern fitting, fixing Accessories and Accessories Set as Jaquar or approved Equal., Sample to architects approval
| Size 370x695x795mm, S Trap-300mm. | No | 2 |  | 0
Wash hand basin-
Installation labour charge of existing wash hand basin : complete with long neck tap, stainless steel bottle trap and all necessary accessories.
| 600 x 400 | No | 2 |  | 0
| repair of angle valve at existing wash hand basin near reception | No | 1 |  | 0
Roll Holders
| Supply and fix stainless steel roll holders as Jaqual or approved equal | No | 2 |  | 0
Soap Dispensor
| Stainless steel soap dispenser as jaguar or approved equal | No | 2 |  | 0
| Carried forward to next page |  |  |  | 0
| Brought forward from previous page |  |  |  | 0
Hand Drier
| Mediclinics Sensor operated hand drier, steel 1.9mm thick one piece cover , chrome bright finish. Size 248 x 278 x 210mm.Effective air flow 330m3/hr Electrical power supply 2.25kW, single phase 240V 50 Hz. | No | 2 |  | 0
Mirror
| Mirror 800X400mm high anti fog backlit mirror with MDF boarder Frames to architect details | No | 2 |  | 0
Water Supply and Distribution
Supply, install, testing and commission of the following;
PPR Pipe PN20 grey colored for cold installation complete with tees, sockets, elbow, threaded adapters, threaded adapters, threaded elbows, reducers and all associated fitting unless as otherwise provided.
Water Supply pipe work
| 25mm Ø pipe | LM | 18 |  | 0
INTERNAL DRAINAGE
| Supply, install, testing and commission of the PVC pipes PN6-63 mm Ø , with tees, bends, reducer, access plugs, clean outs and all necessary fittings including clamps/ brackets for supporting pipes and accessories. | LM | 12 |  | 0
| Carried forward to next page |  |  |  | 0
| Brought forward from previous page |  |  |  | 0
Kitchen Sink
| Kitchen sink: double bowl coated stainless steel sink size 1200mmx600mm complete with 38mm waste plug and chain, 38mm "P" and including fixing base unit cabinet and connection to water supply and waste pipework, bottle trap and all accessories together with stainless steel grating COMPLETE with crome/ brass plaited tap as pegler england for kitchen sinks, angle valves, flexible tube and all connection fitting for correct kitchen sink installation | No | 1 |  | 0
| TOTAL SANITARY FITTINGS AND PLUMBING TO BILL SUMMARY |  |  |  | 0